## Slide 1: Presumed Open Data Data Science Challenge
Feb 2021

## Slide 2: Presumed Open Data Data Science Challenge
Forecast
Solar
Optimise
Battery
Weather
DATA
Forecast
demand
Reduce Peak
SUB-STATION Demand

## Slide 3: Content
Challenge Scenario / Aim
Tasks, Rules & Dates
Site Details
Data Sets
Constraints
Solution Design
Progress
Next Steps
Appendix 1: Technical Design Templates & References

## Slide 4: THE CHALLANGE

## Slide 5: Challenge Scenario
AIM: Reduce Evening Demand over peak (3:30pm to 9pm UTC) via battery discharge. Charge battery before 3pm UTC. Maximise use of Solar.

## Slide 6: Tasks, Rules & Dates

## Slide 7: Site Details
6MWh / 2.5MW battery
5MW solar farm, Stentaway
Devon, southwest England
Substation
Six weather stations, four near substation / PV – two are in the channel
Temp
Irradiance
Panel Temp
Irradiance
Solar Output
Charge
Discharge
SoC
Substation Demand
Site Demand = Solar – Battery Charge

## Slide 8: Data Sets
Substation HH Demand: Needs cleaning for Large Values, Constant Values, Missing Values. In UTC but demand follows local pattern. Available up to start of task week.
PV Generation (Needs cleaning for missing values) hh data in UTC for:
  Average solar output (MW)
  Average irradiance (Wm-2 )
  Panel Temperature (Celsius)
  Available up to start of task week.
Weather Forecast Data NASA’s MERRA-2
  Hourly reanalysis data – i.e. reassimilated forecasts using current observations. ▪ Irradiance (Wm-2 ) ▪ Temperature (Celsius)
  Six sites including four surrounding grid points of substation/PV site
  Starting 1st January 2015
  Up to End of Task Week

## Slide 9: Constraints
Battery Import / Export (2.5MW): −2.5𝑀𝑊 = 𝐵𝑚𝑖𝑛 ≤ 𝐵𝑑,𝑘 ≤ 𝐵𝑚𝑎𝑥 = 2.5𝑀
Battery Capacity (6MWh): 𝐶𝑑,𝑘, (in MWh): 0 ≤ 𝐶𝑑,𝑘 ≤ 𝐶𝑚𝑎𝑥 = 6𝑀𝑊ℎ
Total charge in the battery (State of Charge, SoC) at the next time step 𝐶𝑑,𝑘+1 is related to how much is currently in the battery and how much charged within the battery at time k, i.e. 𝐶𝑑,𝑘+1 = 𝐶𝑑,𝑘 + 0.5𝐵𝑑,
Battery Charging (𝐵𝑑,𝑘 ≥ 0) is only allowed from midnight to 3.30PM (𝑘 = 1 𝑡𝑜 31)
Battery Discharging (𝐵𝑑,𝑘 ≤ 0) is only allowed from 3.30PM to 9PM 𝑘 = 32 𝑡𝑜 42
Battery must start empty at the start of each day in the test week. I.e. 𝐶𝑑,1 = 0 for 𝑑 = 1, … , 7.
Solar generation is always stored first, remainder from Grid:
𝐵𝑑,𝑘 ≥ 0 be the requested power to be charged into the storage device. If 𝑃𝑑,𝑘 𝑇𝑜𝑡𝑎𝑙 is the total PV average power generated by the solar then one of two scenarios occurs:
  1. If 𝐵𝑑,𝑘 ≤ 𝑃𝑑,𝑘 𝑇𝑜𝑡𝑎𝑙, then all the energy comes from the solar generation.
  2. If 𝐵𝑑,𝑘 > 𝑃𝑑,𝑘 𝑇𝑜𝑡𝑎𝑙, then 𝑃𝑑,𝑘 𝑇𝑜𝑡𝑎𝑙 is stored in the battery from solar generation and 𝐵𝑑,𝑘 − 𝑃𝑑,𝑘 𝑇𝑜𝑡𝑎𝑙 comes from the grid.
proportion of this energy over the day is given by:

## Slide 10: Scoring Function
Reduce Peak Demand
Maximise Charging from Solar since it is consider less carbon intensive than charging from Grid

## Slide 11: SOLUTION DESIGN

## Slide 12: Solution Functional Scoping
Data Load and Storage
Data Cleansing, Categorisation and Enrichment
Solar Forecasting
Demand Forecasting
Battery Optimisation
Results Storage
Results Validation
Self Scoring
Data Visualisation and Exploratory Analysis
Results Export
Historic Demand
Historic PV
Weather Forecast
Asset Static Data - Battery
Asset Static Data - PV
Data Cleanse
DEMAND FORECAST MODEL
PV MODEL
Store Forecasts
Visualise+ Explore Source Data
Raw Data Store
Visualise+ Explore Forecast Data
Visualise+ Explore Optimisation Results
Battery Optimisation Solver
MODEL BACK TEST
Store Optimisation Results
Weather Station Locations
RESULTS VALIDATION
SELF SCORE

## Slide 13: Technical Design
Weather
PV
Demand
Calendar
Task Files
Enrichment Files
Asset Static
Data Merge
Prep Scripts
Demand Forecast
Model
PV Forecast
Model
OPTIMISATION SOLVER
(ITERATIONS TO AUTOMATE)

## Slide 14: Database Design
Asset
Asset ID*
Name
Location Name
Location Long
Location Lat
Type (BATTERY, SOLAR, SUBSTATION, WEATHER STATION
Capacity MWh
Power MW
Created Date
Created By
Calendar
dateTimeUTC
Clock changes
Mapping to Local
Settlement Period Mapping
List by weeks
WD / NWD
Holidays
Demand Training Data
dateTimeUTC
PV Training Data
dateTimeUTC
Weather Training Data
dateTimeUTC
Weather Forecast
dateTimeUTC
PV Forecasts
dateTimeUTC
Demand & PV Forecasts
dateTimeUTC
DemandMW
Otpimisation Results
Task List
Task
From Date
To Date

## Slide 15: IMPLEMENTATION
Progress To Date

## Slide 17
Obvious data errors for cleaning

## Slide 18: Solar Forecast Model V1
Model tendency to under forecast at high output levels
Location 1 and Location 6 strongest influence on Solar Output

## Slide 19: Demand Forecast Model V1
Local Date Time and Season strongest influence on demand

## Slide 20: Battery Optimisation V1 – Optimise by Hand
Method:
Limit Solar used from in any half hour period to reflect forecast uncertainty. This is dynamic based on the amount of PV (if we have lots available we can be more defensive on our charging) - PV Risk Factor 1
Limit Solar used in morning, avoid using solar in periods where the output is below a threshold since more likely to be impacted by forecast error – PV Risk Factor 2
Peak Reduction Target is based on average demand for peak hours minus 6MWh in battery, spread battery discharge to flatten peak hours – Target Peak
In charging period, aim to smooth the new peak to minimise creation of a new strain on the distribution network (not required for challenge) – Peak Smooth Target
In the last half hour before going into the peak, if the battery is not able to fully charge form the PV – top up from Grid HH (k=31) – FromGridMW [ASSUMPTION - One hh is sufficient to fill battery via Grid, may need review for winter months]

## Slide 21
PV Risk Factor 2: Avoid using Solar when at low levels if possible
PV Risk Factor 1: Don’t use the full solar output if possible, since hours are predictable but output is volatile
Solar Peak Output unpredictable
Task 0 – Day 1
Demand Increase due to Charging
Demand Decrease due to Discharge

## Slide 22: Battery Optimisation V1 – Optimise by Hand
Manual Model Tunning:
Self Scoring and Constraint Validation Dashboard used to iteratively refine Risk Factors used and optimise score (assuming perfect forecast)
Observation: Tunning of the Risk Factors can lead to;
    Not fully charging the Asset from PV going into the peak hours
    Not fully discharging the Battery into the peak, sub optimal peak reduction.
    Emptying the battery before the peak is over, leaving the last period as the new peak
Target Peak Too Aggressive, Battery Empty too early – Last HH is not reduced sufficiently
Target Peak not aggressive enough, full battery charge not used remains in battery

## Slide 23: Battery Optimisation V1 – Optimise by Hand
Close to using Grid power near solar ramping
Generally spare solar in peak solar period

## Slide 24: Optimise by Hand Battery Schedule vs Benchmark Forecast
Benchmarking:
Use Task 0 Battery Schedule from Optimise by Hand with ML forecasts of Demand and PV
Score against Benchmark Week (which is the week prior to the Task 0 week – 16-32 July 18)
Observations:
Score for week reduces from 8.89 to 7.199
No periods of using power from Grid, we are close on shoulder periods of Solar ramping
Peak Reduction has reduced from 42% on average to 34%
Can be more aggressive in Charging in Solar Peak
Chance of using Grid power near solar ramping

## Slide 25: Benchmark Week vs Our Forecast

## Slide 26: Task 0 Results

## Slide 27: Task 1
16/10/2018 – 22/10/2018

## Slide 28: Solar Forecast Model V2
Some improvement in match
Chosen different model type, Voting Ensemble (instead of recommended SparseNormalizer)
This seems to have less tendency to under estimate at high values vs Task 0 model

## Slide 29: Demand Forecast Model V1

## Slide 30: Battery Optimisation V2 – Optimise by Hand
Method Improvements:
Solar Shoulders: Added new parameters for managing solar ramping, allows lower percentage of solar to be used during the solar ramping periods – PV Risk Shoulder Level and PV Shoulder Risk Factor
Corrected Scoring: Scoring now aligned to results, divide by 7 and take as percentage

## Slide 31: Task 1 Battery Optimisation V2 – Optimise by Hand

## Slide 32: Task 1 Results
Significant Drop in league position, from 8th to 25th
First days of task we performed particularly badly

## Slide 33: Task 2
2019-03-10 to 2019-03-16

## Slide 34: Solar Forecast Model V3
Solar model appears to be improving with extra data

## Slide 35: Demand Forecast Model V1

## Slide 36: Forecast vs Actual Comparison - Task 1 Week
Poor Solar Forecast for days 1 to 3, errors in peaks not shoulders
Possible 1 hour offset in forecast vs actual
Under Forecast of Peak Demand
Poor Task 1 results for days 1-3 explained via Forecast errors in both Solar and Demand

## Slide 37: Forecast Model Back Test Comparison – Task 1 Week
Big Variations for Task 1 forecast period from the different forecast models
Latest Solar Model seems a much better fit for Task 1 data
All models under forecast peak demand slightly for Task 1

## Slide 38: Battery Schedule vs Actual PV / Demand
Battery Schedule Task 1 vs Actual PV and Actual Demand
Over forecast of PV peaks leads to charge from grid
Under use of solar in ramping hours
Demand peaks are smoothed in forecast, meaning we could have more peak reduction
Over forecast of PV peak leads to Charging from Grid
Under use of PV in early hours
Smoothing of forecast demand peak, reduces peak reduction

## Slide 39: Task 2 Battery Optimisation V3 – Optimise by Hand Run 1

## Slide 40: Task 2 Battery Optimisation V3 – Optimise by Hand Run 2
More use of PV in early hours
Less Use of PV over peak hours, which may be impacted by un- forecast cloud cover

## Slide 41: Next Steps
Forecast Model Tunning:
  Active Data Cleaning [DONE]
  Machine Learning Bespoke Tuning
  Adding Bearings to Weather Station Information
Data Processing Automation:
  Automate Task Data Setup [IN PROGRESS]
  Forecast creation automation
Optimisation Model Improvements:
  Move into Optimisation Solver [NOT DOING]
  Strategy for solar ramping periods [DONE]
  Remove solar ramping period strategy and focus on using low levels of solar throughout day [TOM – DONE]
  New Strategy for Demand Peak Under forecast [RICH]
  Next challenge is winter months so less solar available and more demand, may need new strategy

## Slide 42: Appendix 1 – Architecture Research

## Slide 43: Azure Architecture Templates

## Slide 44: AWS Architecture Templates

## Slide 45: Python Optimisation