## task0ForecastsPVandDemand_Run1
[11 empty] | PeakReductionRd(%) | Solar | Grid | Score
| d | startPeakMW | targetPeakMW | PV Risk Factor 1 | PV Risk Factor 2 | PeakSmoothTarget | peakNewMW | Available Solar | FromSolarMW | FromGridMW |  | pd1 | pd2 | sd
| 1 | 3.2347 | 1.9067 | 90% | 1 | 3.2347 | 1.9067 | 46.4325 | -12 | 0 | 41.06% | 100% | 0 | 1.2317
| 2 | 3.2398 | 1.9197 | 45% | 1 | 3.2398 | 1.9197 | 49.3393 | -12 | 0 | 40.65% | 100% | 0 | 1.2196
| 3 | 3.1616 | 1.8915 | 45% | 1 | 3.1616 | 1.8915 | 51.4494 | -12 | 0 | 41.53% | 100% | 0 | 1.2458
| 4 | 3.1236 | 1.8554 | 42% | 0.35 | 3.436 | 1.8554 | 44.2175 | -12 | 0 | 42.64% | 100% | 0 | 1.2792
| 5 | 3.0739 | 1.8034 | 65% | 0.35 | 3.3813 | 1.8034 | 29.7721 | -12 | 0 | 44.25% | 100% | 0 | 1.3275
| 6 | 3.1635 | 1.836 | 66% | 0.3 | 3.4798 | 1.836 | 30.32 | -12 | 0 | 43.24% | 100% | 0 | 1.2972
| 7 | 3.1954 | 1.8495 | 90% | 0.5 | 3.8345 | 1.8495 | 28.8753 | -12 | 0 | 42.82% | 100% | 0% | 1.2847
|  | Method | 1. Limit solar used from any period to reflect forecast uncertainty, make this dynamic based on amount of PV (if we have lots we can be more defensive on our charging) - PV Risk Factor 1 | [9 empty] | Sfinal | 8.8857
|  |  | 2. Max Peak Reduction possible is based on average demand for peak minus 6MWh in battery, spead battery discharge to flatten peak hours | [9 empty] | Battery Charge MW | 1.4923
|  |  | 3. In charging period, aim to smooth the new peak to minimise cration of a new (not required for challenge?) - PeakSmoothTarget | [9 empty] | Battery Discharge MW | -1.3459
|  |  | 4. If we are not at full SoC going into Peak take some extra from Grid in the last possible HH (k=31) - FromGridMW | [9 empty] | Battery Capacity MWh | 6
k | d | dateTimeUTC | task0ForecastDemandMW | netDemandMW | task0ForecsatPVMW | BATERY NET MW | SoC (MWh) | DischargeMW | ChargeMW | Grid Top Up | Charge from PV | Charge from Grid | imprLimBat
1 | 1 | 2018-07-23 | 1.6982 | 1.6982 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 1 | 2018-07-23 00:30 | 1.6299 | 1.6299 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 1 | 2018-07-23 01:00 | 1.5536 | 1.5536 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 1 | 2018-07-23 01:30 | 1.5158 | 1.5158 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 1 | 2018-07-23 02:00 | 1.5074 | 1.5074 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 1 | 2018-07-23 02:30 | 1.4756 | 1.4756 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 1 | 2018-07-23 03:00 | 1.469 | 1.469 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 1 | 2018-07-23 03:30 | 1.4399 | 1.4399 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 1 | 2018-07-23 04:00 | 1.521 | 1.521 | 0.014316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 1 | 2018-07-23 04:30 | 1.6528 | 1.6528 | 0.014316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 1 | 2018-07-23 05:00 | 1.9571 | 1.9571 | 0.23743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 1 | 2018-07-23 05:30 | 2.2281 | 2.2281 | 0.23743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 1 | 2018-07-23 06:00 | 2.6142 | 2.6142 | 0.53841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
14 | 1 | 2018-07-23 06:30 | 2.7672 | 2.7672 | 0.76786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
15 | 1 | 2018-07-23 07:00 | 2.8303 | 3.2347 | 1.297 | 0.40436 | 0.20218 | 0 | -0.40436 | 0 | -0.40436 | 0 | -2.5 | 0
16 | 1 | 2018-07-23 07:30 | 2.8193 | 3.2347 | 1.4876 | 0.41537 | 0.40987 | 0 | -0.41537 | 0 | -0.41537 | 0 | -2.5 | 0
17 | 1 | 2018-07-23 08:00 | 2.6754 | 3.2347 | 2.0629 | 0.55936 | 0.68955 | 0 | -0.55936 | 0 | -0.55936 | 0 | -2.5 | 0
18 | 1 | 2018-07-23 08:30 | 2.6399 | 3.2347 | 2.2368 | 0.59476 | 0.98693 | 0 | -0.59476 | 0 | -0.59476 | 0 | -2.5 | 0
19 | 1 | 2018-07-23 09:00 | 2.5525 | 3.2347 | 2.5508 | 0.68219 | 1.328 | 0 | -0.68219 | 0 | -0.68219 | 0 | -2.5 | 0
20 | 1 | 2018-07-23 09:30 | 2.5124 | 3.2347 | 2.7332 | 0.72227 | 1.6892 | 0 | -0.72227 | 0 | -0.72227 | 0 | -2.5 | 0
21 | 1 | 2018-07-23 10:00 | 2.5055 | 3.2347 | 2.9782 | 0.72924 | 2.0538 | 0 | -0.72924 | 0 | -0.72924 | 0 | -2.5 | 0
22 | 1 | 2018-07-23 10:30 | 2.4828 | 3.2347 | 3.0133 | 0.75188 | 2.4297 | 0 | -0.75188 | 0 | -0.75188 | 0 | -2.5 | 0
23 | 1 | 2018-07-23 11:00 | 2.4615 | 3.2347 | 3.2302 | 0.77321 | 2.8163 | 0 | -0.77321 | 0 | -0.77321 | 0 | -2.5 | 0
24 | 1 | 2018-07-23 11:30 | 2.418 | 3.2347 | 3.2475 | 0.8167 | 3.2247 | 0 | -0.8167 | 0 | -0.8167 | 0 | -2.5 | 0
25 | 1 | 2018-07-23 12:00 | 2.3753 | 3.2347 | 3.0936 | 0.85944 | 3.6544 | 0 | -0.85944 | 0 | -0.85944 | 0 | -2.5 | 0
26 | 1 | 2018-07-23 12:30 | 2.3423 | 3.2347 | 2.997 | 0.89246 | 4.1006 | 0 | -0.89246 | 0 | -0.89246 | 0 | -2.5 | 0
27 | 1 | 2018-07-23 13:00 | 2.2839 | 3.2347 | 2.9361 | 0.95085 | 4.576 | 0 | -0.95085 | 0 | -0.95085 | 0 | -2.5 | 0
28 | 1 | 2018-07-23 13:30 | 2.2899 | 3.2347 | 2.9205 | 0.94477 | 5.0484 | 0 | -0.94477 | 0 | -0.94477 | 0 | -2.5 | 0
29 | 1 | 2018-07-23 14:00 | 2.2994 | 3.2347 | 2.7894 | 0.93527 | 5.5161 | 0 | -0.93527 | 0 | -0.93527 | 0 | -2.5 | 0
30 | 1 | 2018-07-23 14:30 | 2.3896 | 3.2347 | 2.5859 | 0.84516 | 5.9386 | 0 | -0.84516 | 0 | -0.84516 | 0 | -2.5 | 0
31 | 1 | 2018-07-23 15:00 | 2.5264 | 2.6491 | 2.4481 | 0.12271 | 6 | 0 | -0.12271 | 0 | -0.12271 | 0 | -2.5 | 0
32 | 1 | 2018-07-23 15:30 | 2.7324 | 1.9067 | 2.3819 | -0.82574 | 5.5871 | 0.82574 | 0 | 0 | 0 | 0 | 0 | 2.5
33 | 1 | 2018-07-23 16:00 | 3.0551 | 1.9067 | 2.0553 | -1.1484 | 5.013 | 1.1484 | 0 | 0 | 0 | 0 | 0 | 2.5
34 | 1 | 2018-07-23 16:30 | 3.0732 | 1.9067 | 1.8658 | -1.1665 | 4.4297 | 1.1665 | 0 | 0 | 0 | 0 | 0 | 2.5
35 | 1 | 2018-07-23 17:00 | 3.2347 | 1.9067 | 1.3298 | -1.328 | 3.7657 | 1.328 | 0 | 0 | 0 | 0 | 0 | 2.5
36 | 1 | 2018-07-23 17:30 | 3.2188 | 1.9067 | 1.032 | -1.3121 | 3.1096 | 1.3121 | 0 | 0 | 0 | 0 | 0 | 2.5
37 | 1 | 2018-07-23 18:00 | 3.1201 | 1.9067 | 0.46224 | -1.2134 | 2.5029 | 1.2134 | 0 | 0 | 0 | 0 | 0 | 2.5
38 | 1 | 2018-07-23 18:30 | 3.0528 | 1.9067 | 0.44576 | -1.1461 | 1.9299 | 1.1461 | 0 | 0 | 0 | 0 | 0 | 2.5
39 | 1 | 2018-07-23 19:00 | 2.9703 | 1.9067 | 0.12359 | -1.0636 | 1.3981 | 1.0636 | 0 | 0 | 0 | 0 | 0 | 2.5
40 | 1 | 2018-07-23 19:30 | 2.9263 | 1.9067 | 0.11356 | -1.0196 | 0.88827 | 1.0196 | 0 | 0 | 0 | 0 | 0 | 2.5
41 | 1 | 2018-07-23 20:00 | 2.8408 | 1.9067 | 0.0053365 | -0.93413 | 0.42121 | 0.93413 | 0 | 0 | 0 | 0 | 0 | 2.5
42 | 1 | 2018-07-23 20:30 | 2.7491 | 1.9067 | 0.0053365 | -0.84242 | 0 | 0.84242 | 0 | 0 | 0 | 0 | 0 | 2.5
43 | 1 | 2018-07-23 21:00 | 2.6359 | 2.6359 | 0.0053365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 1 | 2018-07-23 21:30 | 2.4427 | 2.4427 | 0.0053365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 1 | 2018-07-23 22:00 | 2.1536 | 2.1536 | 0.0053365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 1 | 2018-07-23 22:30 | 1.8981 | 1.8981 | 0.0053365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 1 | 2018-07-23 23:00 | 1.801 | 1.801 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 1 | 2018-07-23 23:30 | 1.7037 | 1.7037 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 2018-07-24 | 1.7145 | 1.7145 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 2 | 2018-07-24 00:30 | 1.6426 | 1.6426 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 2 | 2018-07-24 01:00 | 1.5616 | 1.5616 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 2 | 2018-07-24 01:30 | 1.5216 | 1.5216 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 2 | 2018-07-24 02:00 | 1.5174 | 1.5174 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 2 | 2018-07-24 02:30 | 1.4834 | 1.4834 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 2 | 2018-07-24 03:00 | 1.4722 | 1.4722 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 2 | 2018-07-24 03:30 | 1.4393 | 1.4393 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 2 | 2018-07-24 04:00 | 1.5413 | 1.5413 | 0.014316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 2 | 2018-07-24 04:30 | 1.6719 | 1.6719 | 0.014316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 2 | 2018-07-24 05:00 | 1.9568 | 1.9568 | 0.23543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 2 | 2018-07-24 05:30 | 2.2453 | 2.2453 | 0.23543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 2 | 2018-07-24 06:00 | 2.6366 | 2.6366 | 0.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
14 | 2 | 2018-07-24 06:30 | 2.768 | 2.768 | 0.75361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
15 | 2 | 2018-07-24 07:00 | 2.8374 | 3.2398 | 1.2453 | 0.40239 | 0.20119 | 0 | -0.40239 | 0 | -0.40239 | 0 | -2.5 | 0
16 | 2 | 2018-07-24 07:30 | 2.8128 | 3.2398 | 1.4794 | 0.42694 | 0.41466 | 0 | -0.42694 | 0 | -0.42694 | 0 | -2.5 | 0
17 | 2 | 2018-07-24 08:00 | 2.7039 | 3.2398 | 2.0098 | 0.53584 | 0.68258 | 0 | -0.53584 | 0 | -0.53584 | 0 | -2.5 | 0
18 | 2 | 2018-07-24 08:30 | 2.671 | 3.2398 | 2.2107 | 0.56877 | 0.96697 | 0 | -0.56877 | 0 | -0.56877 | 0 | -2.5 | 0
19 | 2 | 2018-07-24 09:00 | 2.5096 | 3.2398 | 2.8782 | 0.73018 | 1.3321 | 0 | -0.73018 | 0 | -0.73018 | 0 | -2.5 | 0
20 | 2 | 2018-07-24 09:30 | 2.4618 | 3.2398 | 2.9952 | 0.77791 | 1.721 | 0 | -0.77791 | 0 | -0.77791 | 0 | -2.5 | 0
21 | 2 | 2018-07-24 10:00 | 2.3512 | 3.2398 | 3.1991 | 0.88852 | 2.1653 | 0 | -0.88852 | 0 | -0.88852 | 0 | -2.5 | 0
22 | 2 | 2018-07-24 10:30 | 2.3255 | 3.2398 | 3.2411 | 0.91426 | 2.6224 | 0 | -0.91426 | 0 | -0.91426 | 0 | -2.5 | 0
23 | 2 | 2018-07-24 11:00 | 2.3258 | 3.2398 | 3.5372 | 0.91392 | 3.0794 | 0 | -0.91392 | 0 | -0.91392 | 0 | -2.5 | 0
24 | 2 | 2018-07-24 11:30 | 2.2973 | 3.2398 | 3.5545 | 0.94245 | 3.5506 | 0 | -0.94245 | 0 | -0.94245 | 0 | -2.5 | 0
25 | 2 | 2018-07-24 12:00 | 2.267 | 3.2398 | 3.6142 | 0.97277 | 4.037 | 0 | -0.97277 | 0 | -0.97277 | 0 | -2.5 | 0
26 | 2 | 2018-07-24 12:30 | 2.2092 | 3.2398 | 3.547 | 1.0305 | 4.5522 | 0 | -1.0305 | 0 | -1.0305 | 0 | -2.5 | 0
27 | 2 | 2018-07-24 13:00 | 2.2481 | 3.2398 | 3.2822 | 0.99167 | 5.0481 | 0 | -0.99167 | 0 | -0.99167 | 0 | -2.5 | 0
28 | 2 | 2018-07-24 13:30 | 2.2401 | 3.2398 | 3.2822 | 0.99969 | 5.5479 | 0 | -0.99969 | 0 | -0.99969 | 0 | -2.5 | 0
29 | 2 | 2018-07-24 14:00 | 2.2201 | 3.1243 | 2.6488 | 0.90418 | 6 | 0 | -0.90418 | 0 | -0.90418 | 0 | -2.5 | 0
30 | 2 | 2018-07-24 14:30 | 2.3421 | 2.3421 | 2.5927 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
31 | 2 | 2018-07-24 15:00 | 2.6055 | 2.6055 | 2.2141 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
32 | 2 | 2018-07-24 15:30 | 2.8244 | 1.9197 | 2.1479 | -0.90467 | 5.5477 | 0.90467 | 0 | 0 |  |  | 0 | 2.5
33 | 2 | 2018-07-24 16:00 | 3.0609 | 1.9197 | 1.9327 | -1.1412 | 4.9771 | 1.1412 | 0 | 0 |  |  | 0 | 2.5
34 | 2 | 2018-07-24 16:30 | 3.0959 | 1.9197 | 1.7595 | -1.1762 | 4.389 | 1.1762 | 0 | 0 |  |  | 0 | 2.5
35 | 2 | 2018-07-24 17:00 | 3.2398 | 1.9197 | 1.1439 | -1.32 | 3.729 | 1.32 | 0 | 0 |  |  | 0 | 2.5
36 | 2 | 2018-07-24 17:30 | 3.2067 | 1.9197 | 0.9431 | -1.287 | 3.0855 | 1.287 | 0 | 0 |  |  | 0 | 2.5
37 | 2 | 2018-07-24 18:00 | 3.1667 | 1.9197 | 0.46652 | -1.247 | 2.462 | 1.247 | 0 | 0 |  |  | 0 | 2.5
38 | 2 | 2018-07-24 18:30 | 3.0569 | 1.9197 | 0.45004 | -1.1372 | 1.8934 | 1.1372 | 0 | 0 |  |  | 0 | 2.5
39 | 2 | 2018-07-24 19:00 | 2.9529 | 1.9197 | 0.12359 | -1.0332 | 1.3768 | 1.0332 | 0 | 0 |  |  | 0 | 2.5
40 | 2 | 2018-07-24 19:30 | 2.9062 | 1.9197 | 0.11356 | -0.98645 | 0.88357 | 0.98645 | 0 | 0 |  |  | 0 | 2.5
41 | 2 | 2018-07-24 20:00 | 2.8634 | 1.9197 | 0.0053365 | -0.94363 | 0.41175 | 0.94363 | 0 | 0 |  |  | 0 | 2.5
42 | 2 | 2018-07-24 20:30 | 2.7432 | 1.9197 | 0.0053365 | -0.82351 | 0 | 0.82351 | 0 | 0 |  |  | 0 | 2.5
43 | 2 | 2018-07-24 21:00 | 2.6373 | 2.6373 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
44 | 2 | 2018-07-24 21:30 | 2.4379 | 2.4379 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
45 | 2 | 2018-07-24 22:00 | 2.1379 | 2.1379 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
46 | 2 | 2018-07-24 22:30 | 1.8783 | 1.8783 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
47 | 2 | 2018-07-24 23:00 | 1.7983 | 1.7983 | 0.0018315 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
48 | 2 | 2018-07-24 23:30 | 1.699 | 1.699 | 0.0018315 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
1 | 3 | 2018-07-25 | 1.7097 | 1.7097 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 3 | 2018-07-25 00:30 | 1.6377 | 1.6377 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 3 | 2018-07-25 01:00 | 1.55 | 1.55 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 3 | 2018-07-25 01:30 | 1.51 | 1.51 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 3 | 2018-07-25 02:00 | 1.5057 | 1.5057 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 3 | 2018-07-25 02:30 | 1.4718 | 1.4718 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 3 | 2018-07-25 03:00 | 1.4655 | 1.4655 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 3 | 2018-07-25 03:30 | 1.4347 | 1.4347 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 3 | 2018-07-25 04:00 | 1.5369 | 1.5369 | 0.0094638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 3 | 2018-07-25 04:30 | 1.6675 | 1.6675 | 0.0094638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 3 | 2018-07-25 05:00 | 1.9609 | 1.9609 | 0.21371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 3 | 2018-07-25 05:30 | 2.2431 | 2.2431 | 0.21371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 3 | 2018-07-25 06:00 | 2.6352 | 2.6352 | 0.47487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
14 | 3 | 2018-07-25 06:30 | 2.7668 | 2.7668 | 0.70432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
15 | 3 | 2018-07-25 07:00 | 2.8475 | 3.1616 | 1.1859 | 0.31408 | 0.15704 | 0 | -0.31408 | 0 | -0.31408 | 0 | -2.5 | 0
16 | 3 | 2018-07-25 07:30 | 2.823 | 3.1616 | 1.4201 | 0.33863 | 0.32635 | 0 | -0.33863 | 0 | -0.33863 | 0 | -2.5 | 0
17 | 3 | 2018-07-25 08:00 | 2.7105 | 3.1616 | 1.8165 | 0.45109 | 0.5519 | 0 | -0.45109 | 0 | -0.45109 | 0 | -2.5 | 0
18 | 3 | 2018-07-25 08:30 | 2.6776 | 3.1616 | 2.0001 | 0.48402 | 0.79391 | 0 | -0.48402 | 0 | -0.48402 | 0 | -2.5 | 0
19 | 3 | 2018-07-25 09:00 | 2.5262 | 3.1616 | 2.8479 | 0.63541 | 1.1116 | 0 | -0.63541 | 0 | -0.63541 | 0 | -2.5 | 0
20 | 3 | 2018-07-25 09:30 | 2.4785 | 3.1616 | 2.9649 | 0.68313 | 1.4532 | 0 | -0.68313 | 0 | -0.68313 | 0 | -2.5 | 0
21 | 3 | 2018-07-25 10:00 | 2.3407 | 3.1616 | 3.1653 | 0.82085 | 1.8636 | 0 | -0.82085 | 0 | -0.82085 | 0 | -2.5 | 0
22 | 3 | 2018-07-25 10:30 | 2.315 | 3.1616 | 3.2177 | 0.84659 | 2.2869 | 0 | -0.84659 | 0 | -0.84659 | 0 | -2.5 | 0
23 | 3 | 2018-07-25 11:00 | 2.2981 | 3.1616 | 3.5039 | 0.86345 | 2.7186 | 0 | -0.86345 | 0 | -0.86345 | 0 | -2.5 | 0
24 | 3 | 2018-07-25 11:30 | 2.2696 | 3.1616 | 3.5212 | 0.89198 | 3.1646 | 0 | -0.89198 | 0 | -0.89198 | 0 | -2.5 | 0
25 | 3 | 2018-07-25 12:00 | 2.2216 | 3.1616 | 3.604 | 0.93996 | 3.6346 | 0 | -0.93996 | 0 | -0.93996 | 0 | -2.5 | 0
26 | 3 | 2018-07-25 12:30 | 2.1622 | 3.1616 | 3.5919 | 0.99937 | 4.1343 | 0 | -0.99937 | 0 | -0.99937 | 0 | -2.5 | 0
27 | 3 | 2018-07-25 13:00 | 2.124 | 3.1616 | 3.5946 | 1.0376 | 4.6531 | 0 | -1.0376 | 0 | -1.0376 | 0 | -2.5 | 0
28 | 3 | 2018-07-25 13:30 | 2.1084 | 3.1616 | 3.5946 | 1.0532 | 5.1796 | 0 | -1.0532 | 0 | -1.0532 | 0 | -2.5 | 0
29 | 3 | 2018-07-25 14:00 | 2.1596 | 3.1616 | 3.6151 | 1.002 | 5.6806 | 0 | -1.002 | 0 | -1.002 | 0 | -2.5 | 0
30 | 3 | 2018-07-25 14:30 | 2.2673 | 2.906 | 3.3772 | 0.63876 | 6 | 0 | -0.63876 | 0 | -0.63876 | 0 | -2.5 | 0
31 | 3 | 2018-07-25 15:00 | 2.4883 | 2.4883 | 2.7884 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
32 | 3 | 2018-07-25 15:30 | 2.6709 | 1.8915 | 2.6544 | -0.77939 | 5.6103 | 0.77939 | 0 | 0 |  |  | 0 | 2.5
33 | 3 | 2018-07-25 16:00 | 3.0317 | 1.8915 | 2.3553 | -1.1403 | 5.0402 | 1.1403 | 0 | 0 |  |  | 0 | 2.5
34 | 3 | 2018-07-25 16:30 | 3.0795 | 1.8915 | 2.1659 | -1.188 | 4.4462 | 1.188 | 0 | 0 |  |  | 0 | 2.5
35 | 3 | 2018-07-25 17:00 | 3.1616 | 1.8915 | 1.1722 | -1.2701 | 3.8111 | 1.2701 | 0 | 0 |  |  | 0 | 2.5
36 | 3 | 2018-07-25 17:30 | 3.1367 | 1.8915 | 0.9874 | -1.2452 | 3.1885 | 1.2452 | 0 | 0 |  |  | 0 | 2.5
37 | 3 | 2018-07-25 18:00 | 3.0936 | 1.8915 | 0.46652 | -1.2021 | 2.5874 | 1.2021 | 0 | 0 |  |  | 0 | 2.5
38 | 3 | 2018-07-25 18:30 | 3.0586 | 1.8915 | 0.45004 | -1.1672 | 2.0038 | 1.1672 | 0 | 0 |  |  | 0 | 2.5
39 | 3 | 2018-07-25 19:00 | 2.9549 | 1.8915 | 0.12359 | -1.0634 | 1.4721 | 1.0634 | 0 | 0 |  |  | 0 | 2.5
40 | 3 | 2018-07-25 19:30 | 2.9131 | 1.8915 | 0.11356 | -1.0217 | 0.96129 | 1.0217 | 0 | 0 |  |  | 0 | 2.5
41 | 3 | 2018-07-25 20:00 | 2.911 | 1.8915 | 0.0053365 | -1.0195 | 0.45152 | 1.0195 | 0 | 0 |  |  | 0 | 2.5
42 | 3 | 2018-07-25 20:30 | 2.7944 | 1.8915 | 0.0053365 | -0.90298 | 2.4129e-05 | 0.90298 | 0 | 0 |  |  | 0 | 2.5
43 | 3 | 2018-07-25 21:00 | 2.6383 | 2.6383 | 0.0053365 | 0 | 2.4129e-05 | 0 | 0 | 0 |  |  | 0 | 0
44 | 3 | 2018-07-25 21:30 | 2.4431 | 2.4431 | 0.0053365 | 0 | 2.4129e-05 | 0 | 0 | 0 |  |  | 0 | 0
45 | 3 | 2018-07-25 22:00 | 2.1571 | 2.1571 | 0.0053365 | 0 | 2.4129e-05 | 0 | 0 | 0 |  |  | 0 | 0
46 | 3 | 2018-07-25 22:30 | 1.904 | 1.904 | 0.0053365 | 0 | 2.4129e-05 | 0 | 0 | 0 |  |  | 0 | 0
47 | 3 | 2018-07-25 23:00 | 1.8035 | 1.8035 | 0.0018315 | 0 | 2.4129e-05 | 0 | 0 | 0 |  |  | 0 | 0
48 | 3 | 2018-07-25 23:30 | 1.7069 | 1.7069 | 0.0018315 | 0 | 2.4129e-05 | 0 | 0 | 0 |  |  | 0 | 0
1 | 4 | 2018-07-26 | 1.7003 | 1.7003 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 4 | 2018-07-26 00:30 | 1.6288 | 1.6288 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 4 | 2018-07-26 01:00 | 1.5478 | 1.5478 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 4 | 2018-07-26 01:30 | 1.5078 | 1.5078 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 4 | 2018-07-26 02:00 | 1.5035 | 1.5035 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 4 | 2018-07-26 02:30 | 1.4696 | 1.4696 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 4 | 2018-07-26 03:00 | 1.4714 | 1.4714 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 4 | 2018-07-26 03:30 | 1.4394 | 1.4394 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 4 | 2018-07-26 04:00 | 1.5212 | 1.5212 | 0.012332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 4 | 2018-07-26 04:30 | 1.6476 | 1.6476 | 0.012332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 4 | 2018-07-26 05:00 | 1.9451 | 1.9451 | 0.23543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 4 | 2018-07-26 05:30 | 2.2284 | 2.2284 | 0.23543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 4 | 2018-07-26 06:00 | 2.6168 | 2.8204 | 0.4847 | 0.20358 | 0.10179 | 0 | -0.20358 | 0 | -0.20358 | 0 | -2.5 | 0
14 | 4 | 2018-07-26 06:30 | 2.7394 | 3.0162 | 0.65906 | 0.2768 | 0.24019 | 0 | -0.2768 | 0 | -0.2768 | 0 | -2.5 | 0
15 | 4 | 2018-07-26 07:00 | 2.8342 | 3.3147 | 1.1441 | 0.48053 | 0.48046 | 0 | -0.48053 | 0 | -0.48053 | 0 | -2.5 | 0
16 | 4 | 2018-07-26 07:30 | 2.8097 | 3.3944 | 1.3923 | 0.58477 | 0.77284 | 0 | -0.58477 | 0 | -0.58477 | 0 | -2.5 | 0
17 | 4 | 2018-07-26 08:00 | 2.6512 | 3.3948 | 1.7704 | 0.74358 | 1.1446 | 0 | -0.74358 | 0 | -0.74358 | 0 | -2.5 | 0
18 | 4 | 2018-07-26 08:30 | 2.6211 | 3.436 | 2.0474 | 0.81484 | 1.5521 | 0 | -0.81484 | 0 | -0.81484 | 0 | -2.5 | 0
19 | 4 | 2018-07-26 09:00 | 2.5842 | 3.436 | 2.7008 | 0.8518 | 1.978 | 0 | -0.8518 | 0 | -0.8518 | 0 | -2.5 | 0
20 | 4 | 2018-07-26 09:30 | 2.5291 | 3.436 | 2.8178 | 0.90691 | 2.4314 | 0 | -0.90691 | 0 | -0.90691 | 0 | -2.5 | 0
21 | 4 | 2018-07-26 10:00 | 2.4412 | 3.436 | 3.0297 | 0.99477 | 2.9288 | 0 | -0.99477 | 0 | -0.99477 | 0 | -2.5 | 0
22 | 4 | 2018-07-26 10:30 | 2.4208 | 3.436 | 3.0821 | 1.0152 | 3.4364 | 0 | -1.0152 | 0 | -1.0152 | 0 | -2.5 | 0
23 | 4 | 2018-07-26 11:00 | 2.3521 | 3.436 | 3.1303 | 1.0839 | 3.9783 | 0 | -1.0839 | 0 | -1.0839 | 0 | -2.5 | 0
24 | 4 | 2018-07-26 11:30 | 2.3136 | 3.436 | 3.1476 | 1.1224 | 4.5395 | 0 | -1.1224 | 0 | -1.1224 | 0 | -2.5 | 0
25 | 4 | 2018-07-26 12:00 | 2.262 | 3.4308 | 2.7829 | 1.1688 | 5.1239 | 0 | -1.1688 | 0 | -1.1688 | 0 | -2.5 | 0
26 | 4 | 2018-07-26 12:30 | 2.242 | 3.3702 | 2.6863 | 1.1283 | 5.688 | 0 | -1.1283 | 0 | -1.1283 | 0 | -2.5 | 0
27 | 4 | 2018-07-26 13:00 | 2.184 | 2.8079 | 2.7144 | 0.62394 | 6 | 0 | -0.62394 | 0 | -0.62394 | 0 | -2.5 | 0
28 | 4 | 2018-07-26 13:30 | 2.1794 | 2.1794 | 2.7144 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
29 | 4 | 2018-07-26 14:00 | 2.1586 | 2.1586 | 2.7523 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
30 | 4 | 2018-07-26 14:30 | 2.283 | 2.283 | 2.5487 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
31 | 4 | 2018-07-26 15:00 | 2.5406 | 2.5406 | 2.1022 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
32 | 4 | 2018-07-26 15:30 | 2.7742 | 1.8554 | 2.036 | -0.91881 | 5.5406 | 0.91881 | 0 | 0 |  |  | 0 | 2.5
33 | 4 | 2018-07-26 16:00 | 3.0404 | 1.8554 | 1.9609 | -1.185 | 4.9481 | 1.185 | 0 | 0 |  |  | 0 | 2.5
34 | 4 | 2018-07-26 16:30 | 3.0774 | 1.8554 | 1.7714 | -1.2221 | 4.337 | 1.2221 | 0 | 0 |  |  | 0 | 2.5
35 | 4 | 2018-07-26 17:00 | 3.1236 | 1.8554 | 1.1546 | -1.2682 | 3.7029 | 1.2682 | 0 | 0 |  |  | 0 | 2.5
36 | 4 | 2018-07-26 17:30 | 3.1091 | 1.8554 | 0.95375 | -1.2538 | 3.0761 | 1.2538 | 0 | 0 |  |  | 0 | 2.5
37 | 4 | 2018-07-26 18:00 | 3.0797 | 1.8554 | 0.42438 | -1.2243 | 2.4639 | 1.2243 | 0 | 0 |  |  | 0 | 2.5
38 | 4 | 2018-07-26 18:30 | 3.0262 | 1.8554 | 0.41081 | -1.1708 | 1.8785 | 1.1708 | 0 | 0 |  |  | 0 | 2.5
39 | 4 | 2018-07-26 19:00 | 2.9197 | 1.8554 | 0.092442 | -1.0644 | 1.3463 | 1.0644 | 0 | 0 |  |  | 0 | 2.5
40 | 4 | 2018-07-26 19:30 | 2.8762 | 1.8554 | 0.082405 | -1.0208 | 0.8359 | 1.0208 | 0 | 0 |  |  | 0 | 2.5
41 | 4 | 2018-07-26 20:00 | 2.7683 | 1.8554 | 0.0053365 | -0.91296 | 0.37942 | 0.91296 | 0 | 0 |  |  | 0 | 2.5
42 | 4 | 2018-07-26 20:30 | 2.6142 | 1.8554 | 0.0053365 | -0.75885 | 0 | 0.75885 | 0 | 0 |  |  | 0 | 2.5
43 | 4 | 2018-07-26 21:00 | 2.6057 | 2.6057 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
44 | 4 | 2018-07-26 21:30 | 2.4085 | 2.4085 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
45 | 4 | 2018-07-26 22:00 | 2.1611 | 2.1611 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
46 | 4 | 2018-07-26 22:30 | 1.9103 | 1.9103 | 0.0053365 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
47 | 4 | 2018-07-26 23:00 | 1.8047 | 1.8047 | 0.0018315 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
48 | 4 | 2018-07-26 23:30 | 1.707 | 1.707 | 0.0018315 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
1 | 5 | 2018-07-27 | 1.7166 | 1.7166 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 5 | 2018-07-27 00:30 | 1.646 | 1.646 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 5 | 2018-07-27 01:00 | 1.5656 | 1.5656 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 5 | 2018-07-27 01:30 | 1.5265 | 1.5265 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 5 | 2018-07-27 02:00 | 1.5165 | 1.5165 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 5 | 2018-07-27 02:30 | 1.4834 | 1.4834 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 5 | 2018-07-27 03:00 | 1.4843 | 1.4843 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 5 | 2018-07-27 03:30 | 1.4549 | 1.4549 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 5 | 2018-07-27 04:00 | 1.5153 | 1.5153 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 5 | 2018-07-27 04:30 | 1.6325 | 1.6325 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 5 | 2018-07-27 05:00 | 1.9388 | 1.9388 | 0.19667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 5 | 2018-07-27 05:30 | 2.2258 | 2.2258 | 0.19667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 5 | 2018-07-27 06:00 | 2.5506 | 2.8003 | 0.38428 | 0.24978 | 0.12489 | 0 | -0.24978 | 0 | -0.24978 | 0 | -2.5 | 0
14 | 5 | 2018-07-27 06:30 | 2.6952 | 3.0584 | 0.55864 | 0.36311 | 0.30645 | 0 | -0.36311 | 0 | -0.36311 | 0 | -2.5 | 0
15 | 5 | 2018-07-27 07:00 | 2.7254 | 3.3562 | 0.97047 | 0.63081 | 0.62185 | 0 | -0.63081 | 0 | -0.63081 | 0 | -2.5 | 0
16 | 5 | 2018-07-27 07:30 | 2.7038 | 3.3813 | 1.1335 | 0.67753 | 0.96062 | 0 | -0.67753 | 0 | -0.67753 | 0 | -2.5 | 0
17 | 5 | 2018-07-27 08:00 | 2.6831 | 3.3813 | 1.3169 | 0.69818 | 1.3097 | 0 | -0.69818 | 0 | -0.69818 | 0 | -2.5 | 0
18 | 5 | 2018-07-27 08:30 | 2.6499 | 3.3813 | 1.5542 | 0.73141 | 1.6754 | 0 | -0.73141 | 0 | -0.73141 | 0 | -2.5 | 0
19 | 5 | 2018-07-27 09:00 | 2.5914 | 3.3813 | 2.1941 | 0.78995 | 2.0704 | 0 | -0.78995 | 0 | -0.78995 | 0 | -2.5 | 0
20 | 5 | 2018-07-27 09:30 | 2.5499 | 3.3813 | 2.3111 | 0.83137 | 2.4861 | 0 | -0.83137 | 0 | -0.83137 | 0 | -2.5 | 0
21 | 5 | 2018-07-27 10:00 | 2.6384 | 3.3813 | 1.9582 | 0.74296 | 2.8576 | 0 | -0.74296 | 0 | -0.74296 | 0 | -2.5 | 0
22 | 5 | 2018-07-27 10:30 | 2.6048 | 3.3813 | 2.0227 | 0.77649 | 3.2458 | 0 | -0.77649 | 0 | -0.77649 | 0 | -2.5 | 0
23 | 5 | 2018-07-27 11:00 | 2.517 | 3.3813 | 1.8047 | 0.86431 | 3.678 | 0 | -0.86431 | 0 | -0.86431 | 0 | -2.5 | 0
24 | 5 | 2018-07-27 11:30 | 2.4731 | 3.3813 | 1.8342 | 0.90822 | 4.1321 | 0 | -0.90822 | 0 | -0.90822 | 0 | -2.5 | 0
25 | 5 | 2018-07-27 12:00 | 2.5874 | 3.3813 | 1.4507 | 0.79393 | 4.529 | 0 | -0.79393 | 0 | -0.79393 | 0 | -2.5 | 0
26 | 5 | 2018-07-27 12:30 | 2.5254 | 3.3813 | 1.4507 | 0.85591 | 4.957 | 0 | -0.85591 | 0 | -0.85591 | 0 | -2.5 | 0
27 | 5 | 2018-07-27 13:00 | 2.4668 | 3.3813 | 1.7742 | 0.91453 | 5.4142 | 0 | -0.91453 | 0 | -0.91453 | 0 | -2.5 | 0
28 | 5 | 2018-07-27 13:30 | 2.4652 | 3.3813 | 1.7534 | 0.91611 | 5.8723 | 0 | -0.91611 | 0 | -0.91611 | 0 | -2.5 | 0
29 | 5 | 2018-07-27 14:00 | 2.3785 | 2.6339 | 2.0479 | 0.2554 | 6 | 0 | -0.2554 | 0 | -0.2554 | 0 | -2.5 | 0
30 | 5 | 2018-07-27 14:30 | 2.5326 | 2.5326 | 1.8479 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
31 | 5 | 2018-07-27 15:00 | 2.7141 | 2.7141 | 0.99276 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
32 | 5 | 2018-07-27 15:30 | 2.8474 | 1.8034 | 0.88567 | -1.044 | 5.478 | 1.044 | 0 | 0 |  |  | 0 | 2.5
33 | 5 | 2018-07-27 16:00 | 3.0283 | 1.8034 | 0.44464 | -1.225 | 4.8655 | 1.225 | 0 | 0 |  |  | 0 | 2.5
34 | 5 | 2018-07-27 16:30 | 3.0739 | 1.8034 | 0.40945 | -1.2706 | 4.2302 | 1.2706 | 0 | 0 |  |  | 0 | 2.5
35 | 5 | 2018-07-27 17:00 | 3.0618 | 1.8034 | 0.30886 | -1.2584 | 3.6011 | 1.2584 | 0 | 0 |  |  | 0 | 2.5
36 | 5 | 2018-07-27 17:30 | 2.9841 | 1.8034 | 0.23781 | -1.1807 | 3.0107 | 1.1807 | 0 | 0 |  |  | 0 | 2.5
37 | 5 | 2018-07-27 18:00 | 2.9565 | 1.8034 | 0.15276 | -1.1532 | 2.4341 | 1.1532 | 0 | 0 |  |  | 0 | 2.5
38 | 5 | 2018-07-27 18:30 | 2.948 | 1.8034 | 0.15064 | -1.1446 | 1.8618 | 1.1446 | 0 | 0 |  |  | 0 | 2.5
39 | 5 | 2018-07-27 19:00 | 2.8007 | 1.8034 | 0.045566 | -0.99737 | 1.3631 | 0.99737 | 0 | 0 |  |  | 0 | 2.5
40 | 5 | 2018-07-27 19:30 | 2.7661 | 1.8034 | 0.045566 | -0.96276 | 0.88176 | 0.96276 | 0 | 0 |  |  | 0 | 2.5
41 | 5 | 2018-07-27 20:00 | 2.7487 | 1.8034 | 0.0053365 | -0.9453 | 0.40911 | 0.9453 | 0 | 0 |  |  | 0 | 2.5
42 | 5 | 2018-07-27 20:30 | 2.6215 | 1.8034 | 0.0053365 | -0.81817 | 2.6226e-05 | 0.81817 | 0 | 0 |  |  | 0 | 2.5
43 | 5 | 2018-07-27 21:00 | 2.6148 | 2.6148 | 0.0053365 | 0 | 2.6226e-05 | 0 | 0 | 0 |  |  | 0 | 0
44 | 5 | 2018-07-27 21:30 | 2.4256 | 2.4256 | 0.0053365 | 0 | 2.6226e-05 | 0 | 0 | 0 |  |  | 0 | 0
45 | 5 | 2018-07-27 22:00 | 2.1711 | 2.1711 | 0.0053365 | 0 | 2.6226e-05 | 0 | 0 | 0 |  |  | 0 | 0
46 | 5 | 2018-07-27 22:30 | 1.9309 | 1.9309 | 0.0053365 | 0 | 2.6226e-05 | 0 | 0 | 0 |  |  | 0 | 0
47 | 5 | 2018-07-27 23:00 | 1.825 | 1.825 | 0.0018315 | 0 | 2.6226e-05 | 0 | 0 | 0 |  |  | 0 | 0
48 | 5 | 2018-07-27 23:30 | 1.7097 | 1.7097 | 0.0018315 | 0 | 2.6226e-05 | 0 | 0 | 0 |  |  | 0 | 0
1 | 6 | 2018-07-28 | 1.756 | 1.756 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 6 | 2018-07-28 00:30 | 1.6649 | 1.6649 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 6 | 2018-07-28 01:00 | 1.5971 | 1.5971 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 6 | 2018-07-28 01:30 | 1.5355 | 1.5355 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 6 | 2018-07-28 02:00 | 1.5135 | 1.5135 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 6 | 2018-07-28 02:30 | 1.4746 | 1.4746 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 6 | 2018-07-28 03:00 | 1.4932 | 1.4932 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 6 | 2018-07-28 03:30 | 1.4608 | 1.4608 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 6 | 2018-07-28 04:00 | 1.4886 | 1.4886 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 6 | 2018-07-28 04:30 | 1.5566 | 1.5566 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 6 | 2018-07-28 05:00 | 1.6935 | 1.6935 | 0.20149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 6 | 2018-07-28 05:30 | 1.8378 | 1.8378 | 0.20149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 6 | 2018-07-28 06:00 | 1.9567 | 2.1787 | 0.33644 | 0.22205 | 0.11103 | 0 | -0.22205 | 0 | -0.22205 | 0 | -2.5 | 0
14 | 6 | 2018-07-28 06:30 | 2.2015 | 2.4505 | 0.37732 | 0.24903 | 0.23554 | 0 | -0.24903 | 0 | -0.24903 | 0 | -2.5 | 0
15 | 6 | 2018-07-28 07:00 | 2.5278 | 2.9608 | 0.65601 | 0.43297 | 0.45202 | 0 | -0.43297 | 0 | -0.43297 | 0 | -2.5 | 0
16 | 6 | 2018-07-28 07:30 | 2.6138 | 3.1884 | 0.87058 | 0.57459 | 0.73932 | 0 | -0.57459 | 0 | -0.57459 | 0 | -2.5 | 0
17 | 6 | 2018-07-28 08:00 | 2.8746 | 3.4798 | 1.2577 | 0.60524 | 1.0419 | 0 | -0.60524 | 0 | -0.60524 | 0 | -2.5 | 0
18 | 6 | 2018-07-28 08:30 | 2.8489 | 3.4798 | 1.4018 | 0.63092 | 1.3574 | 0 | -0.63092 | 0 | -0.63092 | 0 | -2.5 | 0
19 | 6 | 2018-07-28 09:00 | 2.8146 | 3.4798 | 1.3759 | 0.66522 | 1.69 | 0 | -0.66522 | 0 | -0.66522 | 0 | -2.5 | 0
20 | 6 | 2018-07-28 09:30 | 2.7338 | 3.4798 | 1.5129 | 0.74607 | 2.063 | 0 | -0.74607 | 0 | -0.74607 | 0 | -2.5 | 0
21 | 6 | 2018-07-28 10:00 | 2.7167 | 3.4798 | 1.5657 | 0.76315 | 2.4446 | 0 | -0.76315 | 0 | -0.76315 | 0 | -2.5 | 0 | +0.033-(0.00019*2)
22 | 6 | 2018-07-28 10:30 | 2.6717 | 3.4798 | 1.6008 | 0.80815 | 2.8487 | 0 | -0.80815 | 0 | -0.80815 | 0 | -2.5 | 0
23 | 6 | 2018-07-28 11:00 | 2.5626 | 3.4798 | 2.4312 | 0.91728 | 3.3073 | 0 | -0.91728 | 0 | -0.91728 | 0 | -2.5 | 0
24 | 6 | 2018-07-28 11:30 | 2.5262 | 3.4798 | 2.4312 | 0.95366 | 3.7842 | 0 | -0.95366 | 0 | -0.95366 | 0 | -2.5 | 0
25 | 6 | 2018-07-28 12:00 | 2.444 | 3.4798 | 2.4522 | 1.0359 | 4.3021 | 0 | -1.0359 | 0 | -1.0359 | 0 | -2.5 | 0
26 | 6 | 2018-07-28 12:30 | 2.4336 | 3.4798 | 2.4522 | 1.0462 | 4.8252 | 0 | -1.0462 | 0 | -1.0462 | 0 | -2.5 | 0
27 | 6 | 2018-07-28 13:00 | 2.3835 | 3.4798 | 2.1456 | 1.0964 | 5.3734 | 0 | -1.0964 | 0 | -1.0964 | 0 | -2.5 | 0
28 | 6 | 2018-07-28 13:30 | 2.3938 | 3.4798 | 2.2075 | 1.0861 | 5.9164 | 0 | -1.0861 | 0 | -1.0861 | 0 | -2.5 | 0
29 | 6 | 2018-07-28 14:00 | 2.4341 | 2.6013 | 1.8256 | 0.16713 | 6 | 0 | -0.16713 | 0 | -0.16713 | 0 | -2.5 | 0
30 | 6 | 2018-07-28 14:30 | 2.5097 | 2.5097 | 1.6405 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
31 | 6 | 2018-07-28 15:00 | 2.7465 | 2.7465 | 1.3573 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
32 | 6 | 2018-07-28 15:30 | 2.9222 | 1.836 | 1.2502 | -1.0861 | 5.4569 | 1.0861 | 0 | 0 |  |  | 0 | 2.5
33 | 6 | 2018-07-28 16:00 | 3.0558 | 1.836 | 1.0279 | -1.2198 | 4.8471 | 1.2198 | 0 | 0 |  |  | 0 | 2.5
34 | 6 | 2018-07-28 16:30 | 3.0825 | 1.836 | 0.75716 | -1.2465 | 4.2238 | 1.2465 | 0 | 0 |  |  | 0 | 2.5
35 | 6 | 2018-07-28 17:00 | 3.1635 | 1.836 | 0.38152 | -1.3275 | 3.5601 | 1.3275 | 0 | 0 |  |  | 0 | 2.5
36 | 6 | 2018-07-28 17:30 | 3.0565 | 1.836 | 0.31047 | -1.2205 | 2.9498 | 1.2205 | 0 | 0 |  |  | 0 | 2.5
37 | 6 | 2018-07-28 18:00 | 2.9768 | 1.836 | 0.12644 | -1.1408 | 2.3794 | 1.1408 | 0 | 0 |  |  | 0 | 2.5
38 | 6 | 2018-07-28 18:30 | 2.9685 | 1.836 | 0.12005 | -1.1325 | 1.8132 | 1.1325 | 0 | 0 |  |  | 0 | 2.5
39 | 6 | 2018-07-28 19:00 | 2.8521 | 1.836 | 0.017821 | -1.0161 | 1.3051 | 1.0161 | 0 | 0 |  |  | 0 | 2.5
40 | 6 | 2018-07-28 19:30 | 2.7911 | 1.836 | 0.017821 | -0.95504 | 0.82762 | 0.95504 | 0 | 0 |  |  | 0 | 2.5
41 | 6 | 2018-07-28 20:00 | 2.721 | 1.836 | 0.0053365 | -0.88494 | 0.38515 | 0.88494 | 0 | 0 |  |  | 0 | 2.5
42 | 6 | 2018-07-28 20:30 | 2.6063 | 1.836 | 0.0053365 | -0.77026 | 2.303e-05 | 0.77026 | 0 | 0 |  |  | 0 | 2.5
43 | 6 | 2018-07-28 21:00 | 2.5858 | 2.5858 | 0.0053365 | 0 | 2.303e-05 | 0 | 0 | 0 |  |  | 0 | 0
44 | 6 | 2018-07-28 21:30 | 2.3994 | 2.3994 | 0.0053365 | 0 | 2.303e-05 | 0 | 0 | 0 |  |  | 0 | 0
45 | 6 | 2018-07-28 22:00 | 2.1514 | 2.1514 | 0.0053365 | 0 | 2.303e-05 | 0 | 0 | 0 |  |  | 0 | 0
46 | 6 | 2018-07-28 22:30 | 1.9193 | 1.9193 | 0.0053365 | 0 | 2.303e-05 | 0 | 0 | 0 |  |  | 0 | 0
47 | 6 | 2018-07-28 23:00 | 1.8375 | 1.8375 | 0.0018315 | 0 | 2.303e-05 | 0 | 0 | 0 |  |  | 0 | 0
48 | 6 | 2018-07-28 23:30 | 1.7225 | 1.7225 | 0.0018315 | 0 | 2.303e-05 | 0 | 0 | 0 |  |  | 0 | 0
1 | 7 | 2018-07-29 | 1.7609 | 1.7609 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
2 | 7 | 2018-07-29 00:30 | 1.6784 | 1.6784 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
3 | 7 | 2018-07-29 01:00 | 1.5997 | 1.5997 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
4 | 7 | 2018-07-29 01:30 | 1.5391 | 1.5391 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
5 | 7 | 2018-07-29 02:00 | 1.525 | 1.525 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
6 | 7 | 2018-07-29 02:30 | 1.4887 | 1.4887 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
7 | 7 | 2018-07-29 03:00 | 1.4888 | 1.4888 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
8 | 7 | 2018-07-29 03:30 | 1.465 | 1.465 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
9 | 7 | 2018-07-29 04:00 | 1.4287 | 1.4287 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
10 | 7 | 2018-07-29 04:30 | 1.4908 | 1.4908 | 0.0018315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
11 | 7 | 2018-07-29 05:00 | 1.6275 | 1.6275 | 0.028761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
12 | 7 | 2018-07-29 05:30 | 1.6712 | 1.6712 | 0.028761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
13 | 7 | 2018-07-29 06:00 | 1.8583 | 1.8583 | 0.065143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
14 | 7 | 2018-07-29 06:30 | 1.9577 | 1.9577 | 0.075136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
15 | 7 | 2018-07-29 07:00 | 2.3214 | 2.3214 | 0.25268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
16 | 7 | 2018-07-29 07:30 | 2.4575 | 2.4575 | 0.32854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
17 | 7 | 2018-07-29 08:00 | 2.8967 | 3.4179 | 0.57902 | 0.52112 | 0.26056 | 0 | -0.52112 | 0 | -0.52112 | 0 | -2.5 | 0
18 | 7 | 2018-07-29 08:30 | 2.9106 | 3.6526 | 0.82446 | 0.74201 | 0.63156 | 0 | -0.74201 | 0 | -0.74201 | 0 | -2.5 | 0
19 | 7 | 2018-07-29 09:00 | 2.9426 | 3.7402 | 0.88622 | 0.79759 | 1.0304 | 0 | -0.79759 | 0 | -0.79759 | 0 | -2.5 | 0 |  | 1
20 | 7 | 2018-07-29 09:30 | 2.8866 | 3.8345 | 1.0711 | 0.94789 | 1.5043 | 0 | -0.94789 | 0 | -0.94789 | 0 | -2.5 | 0
21 | 7 | 2018-07-29 10:00 | 2.807 | 3.8345 | 1.9388 | 1.0275 | 2.018 | 0 | -1.0275 | 0 | -1.0275 | 0 | -2.5 | 0
22 | 7 | 2018-07-29 10:30 | 2.7859 | 3.8345 | 2.0034 | 1.0485 | 2.5423 | 0 | -1.0485 | 0 | -1.0485 | 0 | -2.5 | 0
23 | 7 | 2018-07-29 11:00 | 2.6661 | 3.8345 | 2.6272 | 1.1684 | 3.1265 | 0 | -1.1684 | 0 | -1.1684 | 0 | -2.5 | 0
24 | 7 | 2018-07-29 11:30 | 2.6566 | 3.8345 | 2.6567 | 1.1779 | 3.7154 | 0 | -1.1779 | 0 | -1.1779 | 0 | -2.5 | 0
25 | 7 | 2018-07-29 12:00 | 2.4609 | 3.8345 | 2.7817 | 1.3735 | 4.4022 | 0 | -1.3735 | 0 | -1.3735 | 0 | -2.5 | 0
26 | 7 | 2018-07-29 12:30 | 2.4071 | 3.8345 | 2.7458 | 1.4274 | 5.1159 | 0 | -1.4274 | 0 | -1.4274 | 0 | -2.5 | 0
27 | 7 | 2018-07-29 13:00 | 2.3421 | 3.8345 | 2.8152 | 1.4923 | 5.8621 | 0 | -1.4923 | 0 | -1.4923 | 0 | -2.5 | 0
28 | 7 | 2018-07-29 13:30 | 2.3473 | 2.6232 | 2.8152 | 0.27589 | 6 | 0 | -0.27589 | 0 | -0.27589 | 0 | -2.5 | 0
29 | 7 | 2018-07-29 14:00 | 2.4318 | 2.4318 | 1.8658 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
30 | 7 | 2018-07-29 14:30 | 2.4993 | 2.4993 | 1.7078 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
31 | 7 | 2018-07-29 15:00 | 2.9161 | 2.9161 | 0.75956 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -2.5 | 0
32 | 7 | 2018-07-29 15:30 | 3.064 | 1.8495 | 0.69126 | -1.2145 | 5.3927 | 1.2145 | 0 | 0 |  |  | 0 | 2.5
33 | 7 | 2018-07-29 16:00 | 3.1196 | 1.8495 | 0.44486 | -1.2701 | 4.7577 | 1.2701 | 0 | 0 |  |  | 0 | 2.5
34 | 7 | 2018-07-29 16:30 | 3.1954 | 1.8495 | 0.3695 | -1.3459 | 4.0847 | 1.3459 | 0 | 0 |  |  | 0 | 2.5
35 | 7 | 2018-07-29 17:00 | 3.1154 | 1.8495 | 0.40916 | -1.2659 | 3.4518 | 1.2659 | 0 | 0 |  |  | 0 | 2.5
36 | 7 | 2018-07-29 17:30 | 3.0468 | 1.8495 | 0.33811 | -1.1973 | 2.8531 | 1.1973 | 0 | 0 |  |  | 0 | 2.5
37 | 7 | 2018-07-29 18:00 | 2.9663 | 1.8495 | 0.26711 | -1.1168 | 2.2947 | 1.1168 | 0 | 0 |  |  | 0 | 2.5
38 | 7 | 2018-07-29 18:30 | 2.9187 | 1.8495 | 0.24639 | -1.0692 | 1.7601 | 1.0692 | 0 | 0 |  |  | 0 | 2.5
39 | 7 | 2018-07-29 19:00 | 2.8456 | 1.8495 | 0.047856 | -0.99618 | 1.262 | 0.99618 | 0 | 0 |  |  | 0 | 2.5
40 | 7 | 2018-07-29 19:30 | 2.7748 | 1.8495 | 0.047856 | -0.92529 | 0.79934 | 0.92529 | 0 | 0 |  |  | 0 | 2.5
41 | 7 | 2018-07-29 20:00 | 2.7059 | 1.8495 | 0.0053365 | -0.85642 | 0.37113 | 0.85642 | 0 | 0 |  |  | 0 | 2.5
42 | 7 | 2018-07-29 20:30 | 2.5916 | 1.8495 | 0.0053365 | -0.74217 | 4.6122e-05 | 0.74217 | 0 | 0 |  |  | 0 | 2.5
43 | 7 | 2018-07-29 21:00 | 2.5711 | 2.5711 | 0.0053365 | 0 | 4.6122e-05 | 0 | 0 | 0 |  |  | 0 | 0
44 | 7 | 2018-07-29 21:30 | 2.3953 | 2.3953 | 0.0053365 | 0 | 4.6122e-05 | 0 | 0 | 0 |  |  | 0 | 0
45 | 7 | 2018-07-29 22:00 | 2.1457 | 2.1457 | 0.0053365 | 0 | 4.6122e-05 | 0 | 0 | 0 |  |  | 0 | 0
46 | 7 | 2018-07-29 22:30 | 1.913 | 1.913 | 0.0053365 | 0 | 4.6122e-05 | 0 | 0 | 0 |  |  | 0 | 0
47 | 7 | 2018-07-29 23:00 | 1.801 | 1.801 | 0.0018315 | 0 | 4.6122e-05 | 0 | 0 | 0 |  |  | 0 | 0
48 | 7 | 2018-07-29 23:30 | 1.7037 | 1.7037 | 0.0018315 | 0 | 4.6122e-05 | 0 | 0 | 0 |  |  | 0 | 0

## BenchmarkDemand
dateTimeUTC | rawDemand_mw | settlementPeriod | timeOfDayLocal | bankHoliday | workingDay
2018-07-16 00:30 | 1.62 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-16 01:00 | 1.56 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-16 01:30 | 1.48 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-16 02:00 | 1.48 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-16 02:30 | 1.48 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-16 03:00 | 1.48 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-16 03:30 | 1.48 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-16 04:00 | 1.55 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-16 04:30 | 1.7 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-16 05:00 | 2 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-16 05:30 | 2.22 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-16 06:00 | 2.54 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-16 06:30 | 2.69 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-16 07:00 | 2.87 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-16 07:30 | 2.87 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-16 08:00 | 2.82 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-16 08:30 | 2.79 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-16 09:00 | 2.65 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-16 09:30 | 2.56 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-16 10:00 | 2.56 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-16 10:30 | 2.52 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-16 11:00 | 2.74 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-16 11:30 | 2.85 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-16 12:00 | 2.73 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-16 12:30 | 2.7 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-16 13:00 | 2.62 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-16 13:30 | 2.47 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-16 14:00 | 2.55 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-16 14:30 | 2.78 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-16 15:00 | 2.82 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-16 15:30 | 2.9 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-16 16:00 | 3.12 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-16 16:30 | 3.14 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-16 17:00 | 3.1 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-16 17:30 | 3.08 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-16 18:00 | 3.05 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-16 18:30 | 2.96 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-16 19:00 | 2.84 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-16 19:30 | 2.82 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-16 20:00 | 2.75 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-16 20:30 | 2.75 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-16 21:00 | 2.63 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-16 21:30 | 2.37 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-16 22:00 | 2.09 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-16 22:30 | 1.86 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-16 23:00 | 1.82 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-16 23:30 | 1.74 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-17 | 1.71 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-17 00:30 | 1.61 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-17 01:00 | 1.56 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-17 01:30 | 1.47 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-17 02:00 | 1.47 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-17 02:30 | 1.47 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-17 03:00 | 1.47 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-17 03:30 | 1.47 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-17 04:00 | 1.59 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-17 04:30 | 1.67 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-17 05:00 | 1.99 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-17 05:30 | 2.24 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-17 06:00 | 2.62 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-17 06:30 | 2.8 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-17 07:00 | 2.89 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-17 07:30 | 2.82 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-17 08:00 | 2.84 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-17 08:30 | 2.72 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-17 09:00 | 2.57 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-17 09:30 | 2.54 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-17 10:00 | 2.34 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-17 10:30 | 2.38 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-17 11:00 | 2.53 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-17 11:30 | 2.51 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-17 12:00 | 2.51 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-17 12:30 | 2.38 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-17 13:00 | 2.27 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-17 13:30 | 2.18 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-17 14:00 | 2.26 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-17 14:30 | 2.35 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-17 15:00 | 2.56 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-17 15:30 | 2.92 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-17 16:00 | 3.09 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-17 16:30 | 3.11 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-17 17:00 | 3.24 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-17 17:30 | 3.21 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-17 18:00 | 3.15 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-17 18:30 | 3.05 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-17 19:00 | 3 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-17 19:30 | 2.89 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-17 20:00 | 2.82 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-17 20:30 | 2.84 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-17 21:00 | 2.64 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-17 21:30 | 2.37 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-17 22:00 | 2.07 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-17 22:30 | 1.81 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-17 23:00 | 1.77 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-17 23:30 | 1.65 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-18 | 1.65 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-18 00:30 | 1.61 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-18 01:00 | 1.53 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-18 01:30 | 1.47 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-18 02:00 | 1.47 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-18 02:30 | 1.46 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-18 03:00 | 1.47 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-18 03:30 | 1.47 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-18 04:00 | 1.59 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-18 04:30 | 1.66 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-18 05:00 | 1.94 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-18 05:30 | 2.24 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-18 06:00 | 2.67 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-18 06:30 | 2.91 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-18 07:00 | 2.95 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-18 07:30 | 2.95 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-18 08:00 | 2.95 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-18 08:30 | 3 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-18 09:00 | 2.82 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-18 09:30 | 2.7 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-18 10:00 | 2.78 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-18 10:30 | 2.75 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-18 11:00 | 2.73 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-18 11:30 | 2.62 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-18 12:00 | 2.46 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-18 12:30 | 2.42 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-18 13:00 | 2.42 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-18 13:30 | 2.4 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-18 14:00 | 2.37 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-18 14:30 | 2.48 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-18 15:00 | 2.74 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-18 15:30 | 3.05 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-18 16:00 | 3.18 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-18 16:30 | 3.23 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-18 17:00 | 3.1 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-18 17:30 | 3.22 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-18 18:00 | 3.2 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-18 18:30 | 3.1 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-18 19:00 | 3.02 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-18 19:30 | 2.97 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-18 20:00 | 2.86 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-18 20:30 | 2.83 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-18 21:00 | 2.75 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-18 21:30 | 2.46 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-18 22:00 | 2.13 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-18 22:30 | 1.87 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-18 23:00 | 1.75 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-18 23:30 | 1.63 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-19 | 1.63 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-19 00:30 | 1.61 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-19 01:00 | 1.5 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-19 01:30 | 1.47 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-19 02:00 | 1.47 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-19 02:30 | 1.47 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-19 03:00 | 1.47 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-19 03:30 | 1.47 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-19 04:00 | 1.61 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-19 04:30 | 1.72 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-19 05:00 | 1.98 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-19 05:30 | 2.29 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-19 06:00 | 2.66 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-19 06:30 | 2.91 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-19 07:00 | 2.88 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-19 07:30 | 2.93 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-19 08:00 | 2.81 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-19 08:30 | 2.7 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-19 09:00 | 2.48 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-19 09:30 | 2.42 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-19 10:00 | 2.32 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-19 10:30 | 2.26 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-19 11:00 | 2.33 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-19 11:30 | 2.21 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-19 12:00 | 2.05 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-19 12:30 | 2.11 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-19 13:00 | 2.07 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-19 13:30 | 1.99 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-19 14:00 | 2.03 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-19 14:30 | 2.15 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-19 15:00 | 2.36 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-19 15:30 | 2.63 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-19 16:00 | 2.91 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-19 16:30 | 2.98 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-19 17:00 | 3.13 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-19 17:30 | 3.13 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-19 18:00 | 3.02 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-19 18:30 | 2.96 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-19 19:00 | 2.95 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-19 19:30 | 2.89 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-19 20:00 | 2.82 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-19 20:30 | 2.8 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-19 21:00 | 2.67 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-19 21:30 | 2.41 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-19 22:00 | 2.11 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-19 22:30 | 1.9 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-19 23:00 | 1.74 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-19 23:30 | 1.62 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-20 | 1.64 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-20 00:30 | 1.51 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-20 01:00 | 1.47 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-20 01:30 | 1.43 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-20 02:00 | 1.39 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-20 02:30 | 1.42 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-20 03:00 | 1.41 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-20 03:30 | 1.47 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-20 04:00 | 1.51 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-20 04:30 | 1.64 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-20 05:00 | 1.88 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-20 05:30 | 2.29 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-20 06:00 | 2.55 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-20 06:30 | 2.68 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-20 07:00 | 2.63 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-20 07:30 | 2.68 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-20 08:00 | 2.72 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-20 08:30 | 2.6 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-20 09:00 | 2.48 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-20 09:30 | 2.37 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-20 10:00 | 2.27 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-20 10:30 | 2.22 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-20 11:00 | 2.34 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-20 11:30 | 2.24 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-20 12:00 | 2.2 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-20 12:30 | 2 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-20 13:00 | 2.04 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-20 13:30 | 2.04 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-20 14:00 | 2 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-20 14:30 | 2.09 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-20 15:00 | 2.39 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-20 15:30 | 2.49 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-20 16:00 | 2.8 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-20 16:30 | 2.84 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-20 17:00 | 2.87 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-20 17:30 | 2.95 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-20 18:00 | 2.92 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-20 18:30 | 2.87 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-20 19:00 | 2.82 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-20 19:30 | 2.77 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-20 20:00 | 2.75 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-20 20:30 | 2.73 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-20 21:00 | 2.64 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-20 21:30 | 2.4 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-20 22:00 | 2.16 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-20 22:30 | 1.94 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-20 23:00 | 1.83 | 1 | 2021-01-31 | NOT HOLIDAY | NWD
2018-07-20 23:30 | 1.74 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | NWD
2018-07-21 | 1.72 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | NWD
2018-07-21 00:30 | 1.61 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | NWD
2018-07-21 01:00 | 1.51 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | NWD
2018-07-21 01:30 | 1.47 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | NWD
2018-07-21 02:00 | 1.47 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | NWD
2018-07-21 02:30 | 1.47 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | NWD
2018-07-21 03:00 | 1.47 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | NWD
2018-07-21 03:30 | 1.47 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | NWD
2018-07-21 04:00 | 1.47 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | NWD
2018-07-21 04:30 | 1.5 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | NWD
2018-07-21 05:00 | 1.7 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | NWD
2018-07-21 05:30 | 1.86 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | NWD
2018-07-21 06:00 | 2.12 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | NWD
2018-07-21 06:30 | 2.37 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | NWD
2018-07-21 07:00 | 2.63 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | NWD
2018-07-21 07:30 | 2.84 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | NWD
2018-07-21 08:00 | 2.91 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | NWD
2018-07-21 08:30 | 2.84 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | NWD
2018-07-21 09:00 | 2.83 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | NWD
2018-07-21 09:30 | 2.83 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | NWD
2018-07-21 10:00 | 2.75 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | NWD
2018-07-21 10:30 | 2.74 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | NWD
2018-07-21 11:00 | 2.57 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | NWD
2018-07-21 11:30 | 2.4 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | NWD
2018-07-21 12:00 | 2.4 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | NWD
2018-07-21 12:30 | 2.18 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | NWD
2018-07-21 13:00 | 2.09 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | NWD
2018-07-21 13:30 | 2.01 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | NWD
2018-07-21 14:00 | 2.26 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | NWD
2018-07-21 14:30 | 2.64 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | NWD
2018-07-21 15:00 | 2.66 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | NWD
2018-07-21 15:30 | 2.71 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | NWD
2018-07-21 16:00 | 2.86 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | NWD
2018-07-21 16:30 | 2.98 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | NWD
2018-07-21 17:00 | 3.12 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | NWD
2018-07-21 17:30 | 3.16 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | NWD
2018-07-21 18:00 | 2.99 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | NWD
2018-07-21 18:30 | 2.83 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | NWD
2018-07-21 19:00 | 2.79 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | NWD
2018-07-21 19:30 | 2.71 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | NWD
2018-07-21 20:00 | 2.6 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | NWD
2018-07-21 20:30 | 2.65 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | NWD
2018-07-21 21:00 | 2.54 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | NWD
2018-07-21 21:30 | 2.34 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | NWD
2018-07-21 22:00 | 2.13 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | NWD
2018-07-21 22:30 | 1.95 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | NWD
2018-07-21 23:00 | 1.86 | 1 | 2021-01-31 | NOT HOLIDAY | NWD
2018-07-21 23:30 | 1.74 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | NWD
2018-07-22 | 1.74 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | NWD
2018-07-22 00:30 | 1.62 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | NWD
2018-07-22 01:00 | 1.53 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | NWD
2018-07-22 01:30 | 1.47 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | NWD
2018-07-22 02:00 | 1.47 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | NWD
2018-07-22 02:30 | 1.47 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | NWD
2018-07-22 03:00 | 1.47 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | NWD
2018-07-22 03:30 | 1.47 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | NWD
2018-07-22 04:00 | 1.46 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | NWD
2018-07-22 04:30 | 1.44 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | NWD
2018-07-22 05:00 | 1.5 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | NWD
2018-07-22 05:30 | 1.59 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | NWD
2018-07-22 06:00 | 1.79 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | NWD
2018-07-22 06:30 | 1.99 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | NWD
2018-07-22 07:00 | 2.21 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | NWD
2018-07-22 07:30 | 2.44 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | NWD
2018-07-22 08:00 | 2.6 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | NWD
2018-07-22 08:30 | 2.56 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | NWD
2018-07-22 09:00 | 2.47 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | NWD
2018-07-22 09:30 | 2.43 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | NWD
2018-07-22 10:00 | 2.41 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | NWD
2018-07-22 10:30 | 2.37 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | NWD
2018-07-22 11:00 | 2.29 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | NWD
2018-07-22 11:30 | 2.21 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | NWD
2018-07-22 12:00 | 2.13 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | NWD
2018-07-22 12:30 | 2 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | NWD
2018-07-22 13:00 | 2 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | NWD
2018-07-22 13:30 | 2 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | NWD
2018-07-22 14:00 | 2.04 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | NWD
2018-07-22 14:30 | 2.18 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | NWD
2018-07-22 15:00 | 2.33 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | NWD
2018-07-22 15:30 | 2.55 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | NWD
2018-07-22 16:00 | 2.88 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | NWD
2018-07-22 16:30 | 2.97 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | NWD
2018-07-22 17:00 | 3.01 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | NWD
2018-07-22 17:30 | 3.01 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | NWD
2018-07-22 18:00 | 2.93 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | NWD
2018-07-22 18:30 | 2.82 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | NWD
2018-07-22 19:00 | 2.77 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | NWD
2018-07-22 19:30 | 2.81 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | NWD
2018-07-22 20:00 | 2.71 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | NWD
2018-07-22 20:30 | 2.71 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | NWD
2018-07-22 21:00 | 2.62 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | NWD
2018-07-22 21:30 | 2.4 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | NWD
2018-07-22 22:00 | 2.15 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | NWD
2018-07-22 22:30 | 1.93 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | NWD

## BenchmarkPV
dateTimeUTC | rawPV_power_mw | settlementPeriod | timeOfDayLocal | bankHoliday | workingDay
2018-07-16 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-16 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-16 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-16 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-16 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-16 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-16 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-16 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-16 04:30 | 0.01 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-16 05:00 | 0.07 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-16 05:30 | 0.17 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-16 06:00 | 0.36 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-16 06:30 | 0.95 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-16 07:00 | 1.12 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-16 07:30 | 1.04 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-16 08:00 | 1.45 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-16 08:30 | 1.25 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-16 09:00 | 1.67 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-16 09:30 | 2.3 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-16 10:00 | 2.84 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-16 10:30 | 2.66 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-16 11:00 | 2.81 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-16 11:30 | 1.61 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-16 12:00 | 2.15 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-16 12:30 | 1.48 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-16 13:00 | 1.5 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-16 13:30 | 1.75 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-16 14:00 | 2.58 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-16 14:30 | 1.45 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-16 15:00 | 2.22 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-16 15:30 | 2.54 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-16 16:00 | 2.54 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-16 16:30 | 1.83 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-16 17:00 | 1.52 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-16 17:30 | 1.34 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-16 18:00 | 0.79 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-16 18:30 | 0.36 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-16 19:00 | 0.13 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-16 19:30 | 0.05 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-16 20:00 | 0.01 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-16 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-16 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-16 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-16 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-16 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-16 23:00 | 0 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-16 23:30 | 0 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-17 | 0 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-17 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-17 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-17 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-17 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-17 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-17 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-17 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-17 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-17 04:30 | 0.04 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-17 05:00 | 0.1 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-17 05:30 | 0.21 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-17 06:00 | 0.4 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-17 06:30 | 0.58 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-17 07:00 | 0.74 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-17 07:30 | 1.17 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-17 08:00 | 1.27 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-17 08:30 | 1.74 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-17 09:00 | 2.35 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-17 09:30 | 2.68 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-17 10:00 | 3.41 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-17 10:30 | 3.35 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-17 11:00 | 3.28 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-17 11:30 | 2.8 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-17 12:00 | 2.31 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-17 12:30 | 2.63 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-17 13:00 | 2.73 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-17 13:30 | 2.9 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-17 14:00 | 3.39 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-17 14:30 | 2.96 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-17 15:00 | 3.32 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-17 15:30 | 2.1 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-17 16:00 | 1.84 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-17 16:30 | 1.9 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-17 17:00 | 0.99 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-17 17:30 | 0.64 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-17 18:00 | 0.31 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-17 18:30 | 0.18 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-17 19:00 | 0.11 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-17 19:30 | 0.04 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-17 20:00 | 0 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-17 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-17 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-17 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-17 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-17 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-17 23:00 | 0 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-17 23:30 | 0 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-18 | 0 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-18 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-18 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-18 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-18 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-18 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-18 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-18 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-18 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-18 04:30 | 0.01 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-18 05:00 | 0.07 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-18 05:30 | 0.18 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-18 06:00 | 0.27 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-18 06:30 | 0.53 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-18 07:00 | 0.58 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-18 07:30 | 0.64 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-18 08:00 | 0.43 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-18 08:30 | 0.67 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-18 09:00 | 0.99 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-18 09:30 | 1.55 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-18 10:00 | 1.41 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-18 10:30 | 1.13 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-18 11:00 | 1.33 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-18 11:30 | 1.9 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-18 12:00 | 2.18 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-18 12:30 | 2.46 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-18 13:00 | 2.22 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-18 13:30 | 2.02 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-18 14:00 | 2.22 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-18 14:30 | 2.23 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-18 15:00 | 2.27 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-18 15:30 | 1.81 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-18 16:00 | 1.43 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-18 16:30 | 1.5 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-18 17:00 | 1.16 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-18 17:30 | 1.07 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-18 18:00 | 0.69 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-18 18:30 | 0.4 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-18 19:00 | 0.19 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-18 19:30 | 0.05 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-18 20:00 | 0.01 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-18 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-18 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-18 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-18 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-18 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-18 23:00 | 0 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-18 23:30 | 0 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-19 | 0 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-19 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-19 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-19 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-19 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-19 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-19 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-19 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-19 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-19 04:30 | 0.02 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-19 05:00 | 0.1 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-19 05:30 | 0.23 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-19 06:00 | 0.52 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-19 06:30 | 0.75 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-19 07:00 | 1.16 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-19 07:30 | 0.85 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-19 08:00 | 1.34 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-19 08:30 | 2.2 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-19 09:00 | 2.81 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-19 09:30 | 3.17 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-19 10:00 | 3.35 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-19 10:30 | 3.62 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-19 11:00 | 3.76 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-19 11:30 | 3.79 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-19 12:00 | 3.8 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-19 12:30 | 3.74 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-19 13:00 | 3.8 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-19 13:30 | 3.79 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-19 14:00 | 3.68 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-19 14:30 | 3.49 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-19 15:00 | 3.22 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-19 15:30 | 2.88 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-19 16:00 | 2.49 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-19 16:30 | 1.98 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-19 17:00 | 1.03 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-19 17:30 | 0.94 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-19 18:00 | 0.8 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-19 18:30 | 0.39 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-19 19:00 | 0.18 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-19 19:30 | 0.08 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-19 20:00 | 0.01 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-19 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-19 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-19 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-19 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-19 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-19 23:00 | 0 | 1 | 2021-01-31 | NOT HOLIDAY | WD
2018-07-19 23:30 | 0 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | WD
2018-07-20 | 0 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | WD
2018-07-20 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | WD
2018-07-20 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | WD
2018-07-20 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | WD
2018-07-20 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | WD
2018-07-20 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | WD
2018-07-20 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | WD
2018-07-20 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | WD
2018-07-20 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | WD
2018-07-20 04:30 | 0.03 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | WD
2018-07-20 05:00 | 0.1 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | WD
2018-07-20 05:30 | 0.19 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | WD
2018-07-20 06:00 | 0.36 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | WD
2018-07-20 06:30 | 0.73 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | WD
2018-07-20 07:00 | 1.28 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | WD
2018-07-20 07:30 | 1.76 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | WD
2018-07-20 08:00 | 1.42 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | WD
2018-07-20 08:30 | 1.45 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | WD
2018-07-20 09:00 | 2.51 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | WD
2018-07-20 09:30 | 3.32 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | WD
2018-07-20 10:00 | 3.6 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | WD
2018-07-20 10:30 | 3.76 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | WD
2018-07-20 11:00 | 3.54 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | WD
2018-07-20 11:30 | 3.61 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | WD
2018-07-20 12:00 | 3.63 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | WD
2018-07-20 12:30 | 3.78 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | WD
2018-07-20 13:00 | 3.78 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | WD
2018-07-20 13:30 | 3.73 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | WD
2018-07-20 14:00 | 3.48 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | WD
2018-07-20 14:30 | 3.54 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | WD
2018-07-20 15:00 | 2.77 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | WD
2018-07-20 15:30 | 2.84 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | WD
2018-07-20 16:00 | 2.12 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | WD
2018-07-20 16:30 | 1.67 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | WD
2018-07-20 17:00 | 1.65 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | WD
2018-07-20 17:30 | 0.78 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | WD
2018-07-20 18:00 | 0.57 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | WD
2018-07-20 18:30 | 0.31 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | WD
2018-07-20 19:00 | 0.12 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | WD
2018-07-20 19:30 | 0.02 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | WD
2018-07-20 20:00 | 0 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | WD
2018-07-20 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | WD
2018-07-20 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | WD
2018-07-20 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | WD
2018-07-20 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | WD
2018-07-20 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | WD
2018-07-20 23:00 | 0 | 1 | 2021-01-31 | NOT HOLIDAY | NWD
2018-07-20 23:30 | 0 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | NWD
2018-07-21 | 0 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | NWD
2018-07-21 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | NWD
2018-07-21 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | NWD
2018-07-21 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | NWD
2018-07-21 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | NWD
2018-07-21 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | NWD
2018-07-21 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | NWD
2018-07-21 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | NWD
2018-07-21 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | NWD
2018-07-21 04:30 | 0 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | NWD
2018-07-21 05:00 | 0.1 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | NWD
2018-07-21 05:30 | 0.15 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | NWD
2018-07-21 06:00 | 0.13 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | NWD
2018-07-21 06:30 | 0.27 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | NWD
2018-07-21 07:00 | 0.59 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | NWD
2018-07-21 07:30 | 0.49 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | NWD
2018-07-21 08:00 | 0.72 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | NWD
2018-07-21 08:30 | 1.29 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | NWD
2018-07-21 09:00 | 1.63 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | NWD
2018-07-21 09:30 | 1.88 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | NWD
2018-07-21 10:00 | 2.21 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | NWD
2018-07-21 10:30 | 1.63 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | NWD
2018-07-21 11:00 | 2.15 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | NWD
2018-07-21 11:30 | 3.05 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | NWD
2018-07-21 12:00 | 2.53 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | NWD
2018-07-21 12:30 | 3.62 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | NWD
2018-07-21 13:00 | 2.7 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | NWD
2018-07-21 13:30 | 2.53 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | NWD
2018-07-21 14:00 | 1.1 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | NWD
2018-07-21 14:30 | 0.67 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | NWD
2018-07-21 15:00 | 0.77 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | NWD
2018-07-21 15:30 | 1.52 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | NWD
2018-07-21 16:00 | 1.58 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | NWD
2018-07-21 16:30 | 1.15 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | NWD
2018-07-21 17:00 | 0.51 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | NWD
2018-07-21 17:30 | 0.24 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | NWD
2018-07-21 18:00 | 0.36 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | NWD
2018-07-21 18:30 | 0.3 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | NWD
2018-07-21 19:00 | 0.08 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | NWD
2018-07-21 19:30 | 0.03 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | NWD
2018-07-21 20:00 | 0 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | NWD
2018-07-21 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | NWD
2018-07-21 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | NWD
2018-07-21 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | NWD
2018-07-21 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | NWD
2018-07-21 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | NWD
2018-07-21 23:00 | 0 | 1 | 2021-01-31 | NOT HOLIDAY | NWD
2018-07-21 23:30 | 0 | 2 | 2021-01-31 00:30 | NOT HOLIDAY | NWD
2018-07-22 | 0 | 3 | 2021-01-31 01:00 | NOT HOLIDAY | NWD
2018-07-22 00:30 | 0 | 4 | 2021-01-31 01:30 | NOT HOLIDAY | NWD
2018-07-22 01:00 | 0 | 5 | 2021-01-31 02:00 | NOT HOLIDAY | NWD
2018-07-22 01:30 | 0 | 6 | 2021-01-31 02:30 | NOT HOLIDAY | NWD
2018-07-22 02:00 | 0 | 7 | 2021-01-31 03:00 | NOT HOLIDAY | NWD
2018-07-22 02:30 | 0 | 8 | 2021-01-31 03:30 | NOT HOLIDAY | NWD
2018-07-22 03:00 | 0 | 9 | 2021-01-31 04:00 | NOT HOLIDAY | NWD
2018-07-22 03:30 | 0 | 10 | 2021-01-31 04:30 | NOT HOLIDAY | NWD
2018-07-22 04:00 | 0 | 11 | 2021-01-31 05:00 | NOT HOLIDAY | NWD
2018-07-22 04:30 | 0.02 | 12 | 2021-01-31 05:30 | NOT HOLIDAY | NWD
2018-07-22 05:00 | 0.07 | 13 | 2021-01-31 06:00 | NOT HOLIDAY | NWD
2018-07-22 05:30 | 0.12 | 14 | 2021-01-31 06:30 | NOT HOLIDAY | NWD
2018-07-22 06:00 | 0.29 | 15 | 2021-01-31 07:00 | NOT HOLIDAY | NWD
2018-07-22 06:30 | 0.63 | 16 | 2021-01-31 07:30 | NOT HOLIDAY | NWD
2018-07-22 07:00 | 0.86 | 17 | 2021-01-31 08:00 | NOT HOLIDAY | NWD
2018-07-22 07:30 | 1.32 | 18 | 2021-01-31 08:30 | NOT HOLIDAY | NWD
2018-07-22 08:00 | 1.38 | 19 | 2021-01-31 09:00 | NOT HOLIDAY | NWD
2018-07-22 08:30 | 2.17 | 20 | 2021-01-31 09:30 | NOT HOLIDAY | NWD
2018-07-22 09:00 | 2.86 | 21 | 2021-01-31 10:00 | NOT HOLIDAY | NWD
2018-07-22 09:30 | 3.23 | 22 | 2021-01-31 10:30 | NOT HOLIDAY | NWD
2018-07-22 10:00 | 3.22 | 23 | 2021-01-31 11:00 | NOT HOLIDAY | NWD
2018-07-22 10:30 | 3.74 | 24 | 2021-01-31 11:30 | NOT HOLIDAY | NWD
2018-07-22 11:00 | 3.79 | 25 | 2021-01-31 12:00 | NOT HOLIDAY | NWD
2018-07-22 11:30 | 3.8 | 26 | 2021-01-31 12:30 | NOT HOLIDAY | NWD
2018-07-22 12:00 | 3.8 | 27 | 2021-01-31 13:00 | NOT HOLIDAY | NWD
2018-07-22 12:30 | 3.8 | 28 | 2021-01-31 13:30 | NOT HOLIDAY | NWD
2018-07-22 13:00 | 3.8 | 29 | 2021-01-31 14:00 | NOT HOLIDAY | NWD
2018-07-22 13:30 | 3.79 | 30 | 2021-01-31 14:30 | NOT HOLIDAY | NWD
2018-07-22 14:00 | 3.7 | 31 | 2021-01-31 15:00 | NOT HOLIDAY | NWD
2018-07-22 14:30 | 3.49 | 32 | 2021-01-31 15:30 | NOT HOLIDAY | NWD
2018-07-22 15:00 | 3.21 | 33 | 2021-01-31 16:00 | NOT HOLIDAY | NWD
2018-07-22 15:30 | 2.9 | 34 | 2021-01-31 16:30 | NOT HOLIDAY | NWD
2018-07-22 16:00 | 1.81 | 35 | 2021-01-31 17:00 | NOT HOLIDAY | NWD
2018-07-22 16:30 | 1.26 | 36 | 2021-01-31 17:30 | NOT HOLIDAY | NWD
2018-07-22 17:00 | 1.68 | 37 | 2021-01-31 18:00 | NOT HOLIDAY | NWD
2018-07-22 17:30 | 1.16 | 38 | 2021-01-31 18:30 | NOT HOLIDAY | NWD
2018-07-22 18:00 | 0.69 | 39 | 2021-01-31 19:00 | NOT HOLIDAY | NWD
2018-07-22 18:30 | 0.31 | 40 | 2021-01-31 19:30 | NOT HOLIDAY | NWD
2018-07-22 19:00 | 0.11 | 41 | 2021-01-31 20:00 | NOT HOLIDAY | NWD
2018-07-22 19:30 | 0.04 | 42 | 2021-01-31 20:30 | NOT HOLIDAY | NWD
2018-07-22 20:00 | 0 | 43 | 2021-01-31 21:00 | NOT HOLIDAY | NWD
2018-07-22 20:30 | 0 | 44 | 2021-01-31 21:30 | NOT HOLIDAY | NWD
2018-07-22 21:00 | 0 | 45 | 2021-01-31 22:00 | NOT HOLIDAY | NWD
2018-07-22 21:30 | 0 | 46 | 2021-01-31 22:30 | NOT HOLIDAY | NWD
2018-07-22 22:00 | 0 | 47 | 2021-01-31 23:00 | NOT HOLIDAY | NWD
2018-07-22 22:30 | 0 | 48 | 2021-01-31 23:30 | NOT HOLIDAY | NWD